DANFOSS STARTUP CHEAT SHEET

NOTE: If the parameter is not listed below, leave it as-is

- Quick Menu – Quick Setup

Enter motor info then

3-41 Ramp up – 10s for pumps 60s for fans

3-42 Ramp down – 10s for pumps 60s for fans

4-12 Motor Speed Low – 18Hz

4-14 Motor Speed High – 60Hz

- Quick Menu – Function Setup – Open Loop Settings – Analog Reference

3-02 Minimum Reference – 0Hz

3-03 Maximum Reference – 60Hz

6-14 Terminal 53 Low – 0.000

6-15 Terminal 53 High – 60.000

- Main Menu – 1 Load and Motor

1-03 - Variable Torque

1-29 AMA – Enable Complete AMA

1-73 Flying Start – Disable for pumps/Enable for fans

- Main Menu – 4 Limits/Warnings

4-10 Motor Speed Direction – Clockwise Only for pumps/Both directions for fans

- Main Menu – 15 Drive Information

15-43 – Software Version for paperwork

- For drives with bypass, Terminal X55 1 and 2 is for run permissive (terminal 19 on drive)

3 and 4 is the start command (terminal 18 on drive)

5 and 6 is the external interlock/safety (terminal 27 on drive)